# SECTION 251 – GALVANIC ANODES

## 251.01 – Description

These specifications cover galvanic anodes used to minimize corrosion between the interface of existing concrete and concrete repair materials.

## 251.02 – Detail Requirements

Anodes shall come pre-manufactured and be supplied with integral tie wires for connecting together reinforcing steel. Tie wires shall be in accordance with ASTM A82. Anodes shall contain no corrosive constituents or substances detrimental to reinforcing steel.

The material covering the zinc metal shall be inert to fresh concrete and cover the entire zinc material so that the zinc material is protected from coming into direct contact with the reinforcing steel.

Metallic zinc used in the anodes shall be in compliance with ASTM B418 and shall not contain more than the following impurities:

Copper 		0.01 % maximum

Lead 		0.003 % maximum

Iron 		0.015 % maximum

Cadmium 	0.003 % maximum

Individual anodes shall provide a current density output equal to or greater than 0.05 μA/cm2 (0.32 μA/ in2) at 10 years, based upon manufacturer’s recommended steel surface area for placement. The anodes shall be designed and installed such that the anode has the same embedment depth as the reinforcing steel to which it is attached.

Anodes shall be delivered, stored, handled, and installed according to the manufacturer’s instructions.