Guidelines: For use on all projects where conventional pole-mounted, wall-mounted, high-mast, or overhead sign lighting luminaires are to be installed. This Special Provision does not cover tunnel lights. If a Luminaire Retrieval System is required on the Plans, a Public Interest Finding is required.

SP705-000100-00

VIRGINIA DEPARTMENT OF TRANSPORTATION

SPECIAL PROVISION FOR

LIGHT EMITTING DIODE (LED) LUMINAIRES

July 27, 2018

- Description

This work shall consist of furnishing and installing LED luminaires for roadway lighting systems (conventional poles, wall mounted, high mast, and overhead sign lighting) not including tunnel lighting, in accordance with this Special Provision, as shown on the Plans, and as directed by the Engineer.

- General Requirements

The luminaire shall be designed and assembled by the same manufacturer. The luminaire manufacturer shall be ISO 9001 certified or with a documented quality management system of equal stringency and shall have at least five years of experience in manufacturing LED roadway luminaires.

The Independent laboratory used for the luminaire testing shall be on OSHA’s current list of Nationally Recognized Testing Laboratories (NRTLs). The testing laboratory shall be located within the continental United States or Canada.

The luminaire shall be UL listed or have a documented quality management system of equal stringency. The luminaire shall be DesignLights Consortium (DLC) listed or Energy Star certified.

- Materials

All electrical and electronic components of the luminaire shall be compliant with Restriction of Hazardous Substances (RoHS) Directives.

All electrical and electronic components of the luminaire shall meet IEEE C62.41.1, IEEE C62.41.2, and ANSI C136.2 requirements.

The luminaire shall include quick connect/disconnect plugs between separate electrical and electronic components. Wiring within the electrical enclosure shall be NFPA 70/ NEC compliant.

The luminaire shall use a barrier-type terminal block with three line-side wire connectors (including a ground terminal) for power connection to the luminaire. All terminal positions shall be clearly identified. Each connector shall accept only one conductor and accommodate #8 through #12 AWG wire.

The luminaire operating temperature shall include the range of -40°F (-40°C) to 104°F (40°C), with no lumen de-rating from -4°F (-20°C) through 77°F (25°C). The luminaire shall have a passive cooling method (heat sink).

The contact surface between dissimilar metals shall be in accordance to the Section 700 of the Specifications.

  - Luminaire Housing shall be constructed of aluminum alloy, die-cast or extruded with minimum shell thickness of 0.050 inches (50 mils). Other materials may be used if proven to have equal or greater strength, ultraviolet and corrosion resistance, and are approved by the Engineer.

Bolts, studs, nuts, set screws, washers, and rivets shall be furnished as commercial items suitable for the application and in accordance with the manufacturer’s instructions.

Exposed hardware on the housing including cover and latch shall be stainless steel, zinc, or steel with a zinc alloy electroplate and chromate top coat. Other materials may be used if proven to have equal or greater strength, ultraviolet and corrosion resistance, and are approved by the Engineer.

The housing shall include a corrosion resistant polyester powder coat with a minimum of 2 mil nominal thickness. The finish shall exceed a rating of 8 according to ASTM D1654 after 1000 hours of the salt (fog) testing in accordance with ASTM B117.

If non-metallic materials are used for the housing, the coating may not be required if approved by the Engineer and provided the surface of the housing can demonstrate equal or greater strength, and ultraviolet resistance. The testing procedure shall be in accordance with ASTM G154 or G155.

The housing shall be constructed as one integral piece (with the exception of the high mast luminaire). The electrical and the optical compartment shall not be connected using bolts or any other separable means.

The luminaire housing shall protect the interior against dust, solid objects, and moisture.

The housing shall be designed to allow water shedding and resist the build-up of debris and icicles.

The housing shall have an exterior label stating “LED” and wattage in accordance with ANSI C136.15 and must be visible from the ground.

The housing color shall be gray unless otherwise specified on the Plans.

  - Optical Assembly shall be completely sealed and the ingress protection (IP) shall be rated IP66 or higher.

The LED assembly shall have a minimum L70 of 100,000 hours at the specified LED drive current and ambient temperature of 77°F (25°C) based on a minimum of 10,000 hours of data per IES LM-80 and the IES TM-21.

The optical assembly shall have a color rendering index (CRI) of at least 70

Polymer refractive materials shall be UV-inhibited high impact plastic and lens shall be high-impact borosilicate glass or UV-stabilized acrylic. Other materials may be used if proven to have equal or greater strength, ultraviolet and corrosion resistance, and are approved by the Engineer.

  - Driver shall be secured inside the housing and suitable for use in wet locations.

The driver shall have a dimming control signal of 0 to 10V in accordance with IEC 60929.

The driver shall be rated for operation and storage within an ambient temperature range of                  -40°F (-40°C) to 104°F (40°C) of the luminaire.

The driver shall be UL listed and shall meet FCC electrical interference emission and immunity requirements.

The driver shall conform to the following performance requirements:

- Rated life of 100,000 hours minimum at an ambient temperature of 77°F (25°C).

- Power factor of 0.9 or higher, with total harmonic distortion of 20% or less at full load.

- Minimum efficiency of 90% at maximum load and a minimum efficiency of 85% for the driver operating at 50% power

- Accommodate input voltages of 120V – 277V or 347V – 480V.

- Have thermal overload protection mechanism.

  - Surge Protection Device (SPD) shall be an integral part of the luminaire and the LED power supply. The SPD shall be Type 4 in accordance with UL 1449.

The SPD shall be rated at minimum 10KV/5KA surge level.

The SPD shall operate with no performance degradation within an ambient temperature range of                  -40°F (-40°C) to 104°F (40°C) of the luminaire, 0-95% Relative Humidity (RH), non-condensing.

  - Warranty

The luminaire shall be warranted by the manufacturer for a minimum of 10 years from date of installation against any failure resulting from materials, and defects.

Failure is defined as one or more of the following:

- Significant light output reduction from more than 10% of the LED packages

- Moisture inside the optical assembly

- Lens discoloration

- Driver failure

- Presence of other conditions that do not meet specifications.

  - Additional criteria shall be applied to specific type of luminaires as indicated below:

    - Conventional Pole-mounted Luminaire

      - Shall have a system efficacy of at least 100 lumens/watt.

      - Weight shall not exceed 50 pounds.

      - Effective projected area (EPA) of maximum 3 square feet.

      - Shall conform to the requirements of ANSI C136.31 for vibration and be rated at least 3G.

      - The optical assembly shall be rated correlated color temperature (CCT) of 3000 or 4000 Kelvin (K) in accordance with ANSI C136.37.

      - Shall include a prewired 7-pin twist lock ANSI C136.41-compliant receptacle and a rain-tight shorting cap.

      - Shall be designed to slip-fit onto a nominal 2-inches inside diameter or 2-3/8-inches outside diameter tenon and allow for an insertion of at least 3-1/2 inches, with internal barrier preventing over-insertion of the tenon.

      - Shall include clamp with minimum four appropriate size bolts in accordance with the manufacturer’s instructions, unless otherwise directed by the Engineer.

      - Shall include a leveling device for horizontal or vertical orientation.

      - The housing shall include a door that is easy to open and close, or remove and replace without requiring any tool.

    - Wall mounted Luminaire

      - Shall have a system efficacy of at least 70 lumens/watt.

      - Weight shall not exceed 30 pounds.

      - Conform to the requirements of ANSI C136.31 for vibration and be rated at least 1.5G

      - The optical assembly shall be rated CCT of 3000K or 4000K in accordance with ANSI C136.37.

      - Shall be equipped with 0 to 10V field-adjustable output module for dimming capabilities if required on the Plans or directed by the Engineer.

      - Shall be designed such that it can be mounted onto a vertical flat surface by means of at least three appropriate size bolts with approved chemical or mechanical anchors through the wall side of the housing, in accordance with the manufacturer’s instructions, unless otherwise directed by the Engineer.

      - Shall include a wire entry for the incoming power on the top, bottom, back, or vertical sides as required on the Plans. Each entry shall be pre-manufactured and tapped for a standard conduit connection. Unused entries shall be properly closed with screw type plugs supplied by the manufacturer.

      - The housing shall include a door that is easy to open and close, or remove and replace without requiring any tool.

    - High Mast Luminaire

      - Shall have a system efficacy of at least 100 lumens/watt.

      - Weight shall not exceed 70 pounds.

      - EPA of maximum 3.1 square feet.

      - Conform to the requirements of ANSI C136.31 for vibration and be rated at least 3G

      - The optical assembly shall have a rated CCT of 3000K or 4000K in accordance with ANSI C136.37.

      - Shall include a prewired 7-pin twist lock ANSI C136.41 compliant receptacle and a rain-tight shorting cap.

      - Shall be adjustable and designed to slip-fit onto a mast arm mount from a nominal 1-1/4-inches to 2-inches inside diameter and 1-5/8-inches to 2-3/8-inches outside diameter tenon and allow for an insertion of at least 3-1/2 inches, with an internal barrier preventing over insertion of the tenon.

      - Shall include clamp with at least four bolts specified by the manufacturer unless otherwise directed by the Engineer.

      - The housing shall include a door that is easy to open and close, or remove and replace. The door may require a basic tool (such as a flat-tip or phillips screwdriver) to open and close.

    - Overhead Sign Lighting Luminaire

      - Shall have a system efficacy of at least 70 lumens/watt.

      - Weight shall not exceed 30 pounds.

      - EPA of maximum 0.75 square feet.

      - Conform to the requirements of ANSI C136.31 for vibration and be rated minimum 3G

      - The optical assembly shall be rated CCT of 3000K in accordance with ANSI C136.37.

      - Shall be equipped with 0 to 10V field-adjustable output module for dimming capabilities if required on the Plans or directed by the Engineer.

      - Shall be designed such that it can be installed onto one of the following types (as per the Standard Drawing OSS-1):

- Retrieval system

- Mounting Bracket

      - The housing shall include a door that is easy to open and close, or remove and replace without requiring any tool.

- Procedures

The Contractor shall securely install the luminaires at locations designated on the Plans, in accordance with the manufacturer’s instructions.

Overhead sign lighting luminaires shall be installed as per the Standard Drawing OSS-1. If indicated on the Plans, the sign lighting luminaires shall be mounted on luminaire retrieval systems. The Contractor shall demonstrate the functionality of the luminaire retrieval system in the presence of the Inspector. Sign lighting luminaires to be installed without a luminaire retrieval system shall be attached to luminaire mounting brackets.

High mast luminaire and ring assemblies shall be installed and tested in accordance with Section 705. High mast luminaires shall be rotated to maximize illumination on the road and minimize illumination outside the right-of-way, as indicated on the Plans and as directed by the Engineer.

The Contractor shall perform testing of the electrical components in accordance with Section 705 of the Specifications.

- Measurement and Payment

Conventional luminaire will be measured in units of each and will be paid for at the Contract unit price for the wattage and type specified. This price shall include the luminaire housing, slipfitter, optical assembly, drivers, terminal block, surge protection device, labeling, conductor cables to the termini at the base of the pole or junction box, 7-pin receptacle with shorting cap, photo electric control, adjustments, testing, warranty, and incidental hardware to complete the work.

Wall-mounted luminaire will be measured in units of each and will be paid for at the Contract unit price for the wattage and type specified. This price shall include the luminaire housing, mounting hardware, optical assembly, drivers, terminal block, surge protection device, labeling, conduit, conductor cables to the termini at the junction box, adjustments, testing, warranty, and incidental hardware to complete the work.

High mast luminaire will be measured in units of each and will be paid for at the Contract unit price for the wattage and type specified. This price shall include the luminaire housing, slipfitter, optical assembly, drivers, terminal block, surge protection device, labeling, conductor cables to the termini at the base of the pole or junction box, 7-pin receptacle with shorting cap, photoelectric control, adjustments, testing, warranty, and incidental hardware to complete the work.

High Mast Ring Assembly will be measured in units of each and will be paid for at the contract unit price for the number of luminaires to be installed at that location. This price shall include the luminaire ring, lowering device with head frame and assembly, winch assembly, electric drills, electric raise/lower unit, lowering cables, junction box with prewired terminal block, adjustments, testing and incidental hardware to complete the work.

Sign lighting luminaire will be measured in units of each and will be paid for at the Contract unit price for the wattage and type specified. This price shall include the luminaire housing, mounting hardware, optical assembly, drivers, terminal block, surge protection device, labeling, conduit, conductor cables to the termini at the safety switch or junction box at the base of the structure, 7-pin receptacle with shorting cap, photoelectric control, service entrance head, grounding lug, safety switch, contactor, adjustments, testing, warranty, and incidental hardware to complete the work.

Electrical service, if required, shall be measured in accordance with Section 700 of the Specifications.

Luminaire retrieval systems will be measured in units of each and will be paid for at the Contract unit price per each.  This price shall include the luminaire retrieval system, adjustment, and testing.

Payment will be made under:

| Pay Item | Pay Unit |
| --- | --- |
| Conventional luminaire (wattage and type) | Each |
| Wall mounted luminaire (wattage and type) | Each |
| High mast luminaire (wattage and type) | Each |
| High mast ring assembly (number of luminaires) | Each |
| Sign lighting luminaire (wattage and type) | Each |
| Luminaire retrieval system (structure) | Each |